## Sheet1
Differential Pressure Conversion Calculator
15 psi change out at 100 % rated flow
CARTRIDGE CHANGE?
| OBSERVED DP | % RATED FLOW | CORRECTED DP | YES/NO
| 5 | 70 | 7.7463 | NO
| Vessel Rated Flow | 200
| Vessel Actual Flow | 140
Instructions: read differential pressure from vessel (insert in first column) and actual flow rate. Enter
Actual Flow and Rated Flow into columns and % Rated flow will be calculated. Corrected DP will
be calculated and change out will be determined.
Example: for a 500 gpm vessel flowing at 300 gpm with a 5.0 observed differential pressure the
corrected DP is 9.4.